## Slide 1: Thermal performance of the new superfluid helium vertical test cryostats for magnet tests at CERN
A Vande Craen, M Bajko, V Benda, J-B Deschamps, C Giloux, A Lees, V Parma, F Pasdeloup, O Pirotte
ICEC27-ICMC 2018, Oxford, UK
6th of Septembre 2018 E-05:272
CERN, European Organisation for Nuclear Research, Geneva, Switzerland

## Slide 2: Outline
Introduction
Thermal performances measurements
  Calorimetric measurement in 1.9 K superfluid helium
  Boil-off measurement of 4.5 K saturated helium
Results and discussion
Conclusion

## Slide 3: Cryostats
Two new vertical test cryostats installed and commissioned recently
  Vertical Magnet Test Facility of SM18 hall at CERN
  For magnet testing
    HFM: Fresca 2 demonstrator (L: 2.35 m, D:1.03 m, W: 8 tons)
    Cluster D: HL-LHC injection quadrupoles (L: 4.5 m, D: 0.6 m, W: 8 tons)
  Versatile, for future magnets
Maximum magnet weight
HFM : 15 tons
Cluster D : 18 tons

## Slide 4: Cryostats description
Claudet bath principle
  4.5 K helium bath on top of 1.9 K superfluid helium bath
  Lambda plate for thermal insulation between baths
Design features
  20 K Thermalization and vapour cooling to reduce heat loads to 4.5 K
  Stainless steel lambda plate (instead of G10 usually used)
  Metal to metal contact for leak tightness between baths

## Slide 5: Heat load to the 4.5 K saturated helium
Level decrease rate to calculate boil-off
 |  | (4)
 |  | (4)
Helium level [mm]
Time

## Slide 6: Calorimetric measurement in superfluid helium
Based on internal energy balance
Isothermal bath thanks to high thermal conductivity of superfluid helium
 | (1)
 | (1)
 | (2)
 | (2)
 | (3)
 | (3)
Precisely known injected power
Combine (1) and (2)
Helium mass measurement

## Slide 7: Heat loads to 4.5 K
Performances better than specified
  Better vapour cooling than expected
Cluster D
High heat load during first cool-down
Instrumentation support create thermal bridge (300 K – 4.5 K)
After removal back to nominal (instrumentation in cryostat)
HFM Heat load [W] |  | Cluster D Heat load [W] | 
Measured | Specified | Measured | Specified
8 | 26.5 | 16 | 35
Frost due to thermal bridge to 4.5 K in an instrumentation support

## Slide 8: Heat loads to 1.9 K – Very first tests
Poor thermal performance
Incorrect insertion
Differential thermal contractions
Non conformities of helium vessel
Gaps on lambda plate to cryostat interface (up to 1.6 mm)
Metal to metal: impossible to reach specification (due to large dimensions of cryostats)
Flexible sealing needed
Poor thermal performance
All modification of HFM imported to Cluster D
Use of solid PTFE ring as sealing element
 Solid PTFE not flexible enough
HFM
Cluster D

## Slide 9: Heat loads to 1.9 K – ePTFE gasket tape
Improved performance
Expanded PTFE gasket tape (Gore® DF)
Leak tight to gaseous helium under low compressive force
Depend on magnet weight
HFM
Cluster D

## Slide 10: Heat loads to 1.9 K – ePTFE with grease
Better than specified
Apiezon-N vacuum grease to improve leak tightness
 Drastic reduction of heat loads
Superfluid helium permeate inside gasket
Grease not acceptable for long term operation at CERN
Other solution needed:
Conforming to cryostats irregularities
Large range of magnet weight
 Shall be flexible and strong
HFM
Microstructure of ePTFE (Gore®)

## Slide 11: Heat loads to 1.9 K – Silicone seal
Silicone seal
Good mechanical properties
Cost-effective
Very promising results on small scale
  Mechanical (if in a groove)
  Thermal
 Heat loads close to specification in Cluster D
Seal broken after thermal cycle
Groove in lambda plate needed (machining ongoing)
Cluster D

## Slide 12: Conclusion
Developed and successfully applied test procedure for validating thermal performance of vertical cryostats
After learning curve, HFM and Cluster D now fully operational close to specification
New cost effective sealing solution for superfluid helium developed
R&D effort still ongoing to further reduce power consumption

## Slide 13: Thank you for your attention !

## Slide 15: Spare slides

## Slide 16: Spare slides